## Inspection and test plan
Inspection and test plan (ITP)
Yellow cells are for you to fill in. Free template from Deskely · deskely.com/resources/inspection-and-test-plan-template
Project |  |  | ITP number |  | Revision
Scope of work |  |  | Discipline |  | Applicable specifications and codes
H = Hold point: work stops until the party has inspected and released it. W = Witness point: the party is notified and may attend; work goes on if they do not. R = Review of records. S = Surveillance (spot checks). Example below: piping fabrication and installation. Replace the activities with your own scope.
No. | Activity | Reference document | Acceptance criteria | Verifying record | Frequency | Contr. | Client | TPI | Remarks
1. BEFORE WORK STARTS
1 | Review of drawings and procedures | IFC drawings, project specification | Approved, latest revision | Document transmittal | Once | R | R
2 | Welding procedures (WPS and PQR) | ASME IX or ISO 15614 | Qualified for the materials and thickness range | WPS, PQR | Each WPS | R | R | R
3 | Welder qualifications | ASME IX or ISO 9606 | Valid for the process and position | Welder register | Each welder | R | R
4 | Calibration of inspection and test equipment | Calibration procedure | Valid calibration certificate | Calibration register | Each instrument | R | S
2. MATERIAL RECEIPT
5 | Receiving inspection of pipe, fittings, flanges and valves | Purchase order, material specification | Grade, size, rating and heat number match the certificates | Receiving report, EN 10204 3.1 certificates | Each delivery | H | R
6 | Positive material identification (alloys) | Material specification | Alloy confirmed | PMI report | As specified | W | R
3. FABRICATION AND INSTALLATION
7 | Fit-up inspection | WPS, isometric drawing | Root gap, alignment and bevel within the WPS | Weld log | As specified | S | S
8 | Visual inspection of completed welds | ASME B31.3 or ISO 5817 | No unacceptable imperfections | Weld visual report | 100 % | W | S
9 | Non-destructive testing (RT, UT, MT, PT) | NDT procedures, specification | Acceptance criteria of the code | NDT reports | As specified | R | R | R
10 | Post weld heat treatment, where required | WPS, specification | Time and temperature within the procedure | PWHT chart | Each weld | R | R
11 | Dimensional check of spools | Isometric drawing | Within tolerance | Dimensional report | Each spool | S | S
12 | Pipe supports | Support drawings | Correct type and location | Installation ITR | Each line | S | S
4. TESTING AND COMPLETION
13 | Test pack review before testing | Test pack | Welding, NDT and PWHT complete, category A punch cleared | Test pack checklist | Each test pack | H | H
14 | Hydrostatic or pneumatic test | Test procedure, ASME B31.3 | No leaks; pressure held for the hold period | Pressure test certificate | Each test pack | W | H | W
15 | Reinstatement after the test | Test pack | Blinds removed, gaskets and bolting to specification | Reinstatement record | Each test pack | W | W
16 | Painting and coating | Painting specification | Dry film thickness and adhesion within specification | Coating report | As specified | W | S
17 | Final documentation | Project specification | All records complete and signed | Handover dossier | Each system | R | H | R
YOUR ADDITIONAL ACTIVITIES
18
19
20
21
22
23
Sign-off |  | Name | Company |  | Signature |  | Date
Contractor
Client
Third party